## Slide 1: Challenges Encountered While Replacing the SNS Ring Injection Dump Beam Stop and Window
Ryan Schultz
Jeff Saunders
Dave Willis

## Slide 2: SNS is a megawatt-class, accelerator-based pulsed neutron source
~1 GeV protons are injected into a liquid mercury target at 60 Hz
Currently upgrading to 2MW

## Slide 3: SNS Ring Injection Dump (RID) Overview
SNS has three dumps
  Linac, Extraction & RID
  Both the Linac & Extraction dumps are passive (no cooling) with an average power limit of 7.5kW
The RID is designed for continuous use accepting any portion of the HEBT beam not fully stripped
  Nominally 2-10% of the injected beam with an average power of 50-60 kW
  Power limit 150 kW
RID
Linac
Extraction
Target
Accumulator

## Slide 4: Ring Injection Dump Imaging System - Motivation
Uncertainty about beam position and density
Accurate measurement of beam size will improve RID window lifetimes, improve stability of operation
Requires replacement of the existing vacuum window
  Requires luminescent coating

## Slide 5: Florescent Coating… same coating as Target nose
s
RID Vacuum Window
Mercury Target

## Slide 6: Imaging System
Off-Axis Schmidt-Cassegrain Telescope Ready to Operate
Images From Telescope With Optical Testing at Distance of 35 feet
Image
Test Setup

## Slide 7: Beam Stop and Window Replacement
Imaging System required replacing both Beam Stop and Window
Both originally installed in ~2006
  Hands on, NOT remotely
Vacuum window
  Requires 1 e-7 torr
  Remote connection of clamp will be difficult
Beam stop
Window

## Slide 8: Cross section
4.3m
(14 ft)
Beam Stop
Window
Window
Clamp
Vacuum
Pipe

## Slide 9: Hatch Enclosure
High dose rates requires remote handing
  Cameras, borescope, long handled tools, etc.
28 mSv/hr
(2800 mR/hr
16 Sv/hr
(1600 R/hr)
Beam Stop
Window
0.28 mSv/hr
(28 mR/hr)

## Slide 10: Mobile Crane
No building crane.
  Mobile crane through hatch
Communicate 2-way radio

## Slide 11: Remote Handling Zip Lift (Fastorq)
Rated for 15 Ton
  Electrical and pneumatic release
  Mechanical release cable
Shielding & Components
Electric Release

## Slide 12: Radiation Safety Plan
16 Sv/hr
28 mSv/hr
62 mSv total estimate
    6200 mR
    Across 10-15 workers

## Slide 13: Beam Stop Replacement
New Beam Stop Install
Old Beam Stop Removal
No problems

## Slide 14: Vacuum Window Layout
Cage
Roller Bearings
and Rails
Window Assembly
9 cm
(3.5”)
Vacuum
Clamp
Clamp Nuts
Uses Helicoflex seal

## Slide 15: Window Removal Steps
9 cm
9 cm
Cut pipes
Inspect
& Polish?
Vacuum
Sealing
Surface
Move
Cage
Open
Vacuum Clamp
Remove
Window
Install New Window
9 cm

## Slide 16: Window Tool
Force
Movement
3.3m
2 m
Friction
Designed during construction
  (2005)
  Raises/lowers window
  Opens/closes clamp (long sockets)
  Moves cage 9 cm
Worked fine during testing
  Under ideal circumstances
  Original window installation was not tightened using the window tool
  Clamp was tightened directly

## Slide 17: Mock Up Testing
Tested in 2006 & 2023
  No problems
Tested
  Raise/lower window
  Move cage
  Engage clamp

## Slide 18: Window Cage & Rollers
New Steel Roller Bearings
Cage & Rollers
Rusty Steel Roller Bearings

## Slide 19: Enclosure Flooded
Enclosure is back-filled with He during operation
  Since 2006
  Should prevent rust
Enclosure was built before building above it was erected
  Under water for weeks/months during construction
  Rust began before 2006
Window cage installed before beam stop and cooling cradle
  Window clamp assembled by hand

## Slide 20: Window Tool
8-9 kN
5-6 kN
3.3m
2 m
Window Tool can’t provide force required to overcome friction from rust
  It flexes (made out of aluminum)
  Jacking mechanism insufficient
Tried to lift up and move
  Reduce friction force
  Did not work
(1100-1200 lb)
(1800-1900 lb)

## Slide 21: Wedges on long poles
Different Thicknesses
  12 cm (1/2”) at a time
  Were able to move it 9 cm, took days

## Slide 22: Window Removal
Wasn’t easy, but we got it out
  Clamp interfered with window flange
  Minimal clearance radially
Extensive use of borescope
    Observe radial clearance/interference
    Watch remote tools being used
Old Window
Into cask…

## Slide 23: Problems with the Clamp
16 mm movement
25 mm
17 mm
Clamp moves In-Out freely
  Allows yaw rotation
  Becomes oblong when open
Doesn’t open enough
  Only 3-5 mm clearance
Window must be < 8 mm in/out for engagement (all the way around)
Window can rotate freely on pedestal
  Pitch and yaw
Closed Position
Open Position
yaw
pitch
Mock Up

## Slide 24: Window Installation
New vacuum seal designed & fabricated
  Diamond cross section
Constrain pedestal rotation
New Window
Going in…
Diamond Seal Cross Section
1100 Al

## Slide 25: Now the fun begins:
9 cm
After lowering window in place:
  Had to use wedges to move it back – 12 mm at a time
  Flange-Clamp vertical misalignment
    Had to remove window, and shim the window pedestal 2.5 mm down
  Alignment was very challenging
    Window pitch & yaw
    Clamp fore-aft & yaw
    Hours and hours of trial and error
    Borescope and long handled tools
After much struggle, we finally got it clamped!

## Slide 26: Vacuum Test
1e-7 Torr Required
1e-9 Torr L/s Achieved!

## Slide 27: Radiation Safety Plan
16 Sv/hr
28 mSv/hr
62 mSv total estimate
    6200 mR
15 mSv total dose received
    1500 mR
    Across ~10 workers

## Slide 28: What about the rusty rollers?!?
Clamp must be removed FIRST, before removing cage
  But the cage captures the clamp
  Must be removed simultaneously using removal tool
Steps:
  Remove clamp/cage
  Install new modified cage/rollers
  Replace clamp

## Slide 29: Conclusion
Window design has too much compliance for remote installation
  Window pedestal moved too much (pitch, yaw)
Window Tool originally designed was not sufficient
  Clamp mounting allowed too much movement (fore/aft, yaw)
  Able to move cage in ideal conditions, but not with rusted rollers
Despite these challenges, were able to mate up window
  New diamond seal design worked great!
  Did NOT replace rusty rollers, but have a design solution if needed.
Extensive ALARA planning and careful execution
  Received ~25% of estimated dose
Successfully changed RID Beam Stop & Window
  Through much perseverance! It took 8 weeks.
Currently installing new RID Imaging System – startup July 2024